PHASE 2 DELIVERABLE

Variable and Constraint Reference

Quick reference card for pyomo_DTC_CPLEX_TES.py

This reference card maps every Pyomo variable, parameter, and constraint introduced by the TES module back to its physical meaning and to the Phase 1 governing equation that motivates it. Variables and parameters that are inherited from the original DTC_CPLEX dispatch model (BESS, LDES, gas blocks, load) are documented in Greg's existing PtXv3 reference and are not duplicated here.

# Decision variables

Decision variables are the unknowns the optimizer solves for in each hour.

| Variable | Type | Units | Physical meaning | Phase 1 equation |
| --- | --- | --- | --- | --- |
| TCt[t] | Continuous | kW thermal | TES charging power: heat flowing into the storage core from the resistance heaters in hour t. | 1 (heater) |
| TDt[t] | Continuous | kW thermal | TES discharge power: heat flowing from the storage core into the heat exchanger in hour t. | 3 (HX) |
| TXt[t] | Continuous | kWh thermal | TES state of charge: thermal energy stored at the end of hour t. | 2 (SOC) |
| lTvt[t] | Continuous | kW thermal | TES charging loss: heat dissipated during charging that does not couple into the storage core. | 1 and 2 |
| Gtest[t] | Continuous | kW electrical | Steam turbine electrical output in hour t. | 4 (turbine) |
| Kstt[t] | Binary | 0 or 1 | Steam turbine commitment: 1 if turbine is on, 0 if off. | Turndown constraint |

# Parameters

Parameters are constants read from the scenario workbook (gjt_working.xlsx, TES tab) or derived from inputs to py_dtc_cfe.

| Parameter | Source | Default | Physical meaning |
| --- | --- | --- | --- |
| TDmax | svar['tesD_kW'] | scenario | Rated thermal discharge power of the heat exchanger. |
| TCmax | TDmax · tes_CDratio | 3 × TDmax | Rated thermal charge power of the resistance heaters. |
| TXmax | TDmax · tes_duration | scenario | Rated thermal storage capacity (full state of charge). |
| Teff | vars['tes_rte'] | 0.90 | TES round trip efficiency; folds charge side and storage cycle losses. |
| T3max | TDmax · tes_st_eff | 0.40 × TDmax | Rated electrical output of the steam turbine. |
| T3min | T3max · tes_st_min | 0.40 × T3max | Minimum stable electrical output (turbine turndown floor). |
| GTeff | vars['tes_st_eff'] / 100 | 0.40 | Steam turbine thermal to electrical conversion efficiency. |
| TXi | carried forward | tes_kWh × tes_soci | Initial TES state of charge at the start of each rolling window. |

# Constraints

Constraints define the relationships among variables that the optimizer must satisfy in every hour.

| Constraint | Pyomo name | Expression | What it enforces |
| --- | --- | --- | --- |
| TES charging loss | c_tes_loss | lTvt[t] = TCt[t] · (1 - Teff) | Heat lost during charging proportional to charging rate. |
| TES state of charge | c_tes_soc | TXt[t] = TXt[t-1] + TCt[t] - lTvt[t] - TDt[t] | Conservation of energy across the TES boundary. |
| TES capacity limit | c_tes_xmax | TXt[t] <= TXmax | State of charge bounded by rated storage capacity. |
| TES charge limit | c_tes_cmax | TCt[t] <= TCmax | Charging rate bounded by rated heater capacity. |
| TES discharge limit | c_tes_dmax | TDt[t] <= TDmax | Discharge rate bounded by heat exchanger capacity. |
| Steam turbine efficiency | c_st_eff | Gtest[t] = TDt[t] · GTeff | Electrical output equals thermal input times turbine efficiency. |
| Steam turbine upper bound | c_st_max | Gtest[t] <= T3max · Kstt[t] | Output is zero if turbine is off, bounded above by rated when on. |
| Steam turbine lower bound | c_st_min | Gtest[t] >= T3min · Kstt[t] | Output is zero if turbine is off, bounded below by min load when on. |

# Electricity balance contribution

The TES module contributes two terms to the system wide electricity balance constraint c1.

| Side of balance | TES contribution | Meaning |
| --- | --- | --- |
| Supply | Gtest[t] | Steam turbine electrical output flowing into the AC bus. |
| Demand | TCt[t] | Charging power drawn from the AC bus into the resistance heaters. |

# Output time series

After solving, the module returns a results dictionary with one time series per variable. The TES specific time series are the six decision variables listed in the first table above, indexed by hour.